VERTICAL “VHS” SIZE 10-36 STACK

WATER SOURCE HEAT PUMP SPECIFICATIONS

Rev. April 02, 2007

General:

Furnish and install ClimateMaster Water Source Heat Pumps, as indicated on the plans with capacities and characteristics as listed in the schedule and the specifications that follow.

Vertical Stack Water Source Heat Pumps:

Units shall be low range, 40° to 110°F (4.4° to 43.3°C) entering water temperature for low temperature application.  Equivalent units from other manufacturers can be proposed provided approval to bid is given 10 days prior to bid closing.  All equipment listed in this section must be rated and certified in accordance with American Refrigeration Institute / International Standards Organization (ARI / ISO) and Environmental Testing Laboratories for United States and Canada (ETL-US-C).  The units shall have ARI / ISO and ETL-US-C labels.  All cabinets  shall be factory tested under normal operating conditions, risers shall be pressure tested and chassis shall be factory tested under normal operating conditions and water flow rates.  Units tested without water flow are not acceptable.

Basic Construction:

The cabinet panels shall be fabricated from heavy gauge galvanized steel. The rigid one-piece cabinet shall be constructed so that it is self-supporting, and can be installed long before the chassis arrival, and to be able to avoid damage during construction.  Top, base, fan deck, and other metal structural parts are to be 16 gauge construction, while exterior panels to be 20 gauge; unit further strengthened by structural breaks at corners.  Units not constructed of a minimum of these thicknesses are not acceptable. Cabinet shall have a top panel and a bottom panel for structural rigidity of the cabinet; no “open” top or “open” bottom designs allowed.

The cabinet base shall contain a secondary drain pan fully insulated with a pressure differential drain trap connected to the condensate riser pipe, and guide rails for the slide-in refrigeration chassis. Drain pan(s) shall be easily accessible for cleaning. All interior surfaces shall be lined with 1/2 inch (12.7mm) thick, dual density 1-3/4 lb/ft3 (28 kg/m3) acoustic type fiberglass insulation. All fiberglass shall be coated and have exposed edges butted up to flanges to prevent the introduction of glass fibers into the air stream.

Standard cabinet panel insulation must meet NFPA 90A requirements, air erosion and mold growth limits of UL-181, stringent fungal resistance test per ASTM-C1071 and ASTM G21, and shall meet zero level bacteria growth per ASTM G22. Unit insulation must meet these stringent requirements or unit(s) will not be accepted.

Cabinet arrangements shall allow symmetrical placement of riser piping on any of the three sides of the cabinet not used for the chassis access. All Cabinet openings shall have dry wall flanges on all sides. Supply air openings shall be factory cut and flanged as shown on plans. For air noise attenuation purposes, the discharge air from fan shall discharge into insulated plenum that also contains insulated air baffles at all cabinet supply air openings. Units not having supply air noise baffles are not acceptable. Cabinet design shall allow a full height base board (5 inches/127mm) beneath the chassis access. The cabinet shall contain an easily removable motor/blower assembly.

Full length supply, return, and insulated condensate water risers shall be type M copper with integral internal piping including ball valves (for shut off purposes at unit). Field installed hose kits are required to connect the chassis piping to the cabinet piping.  The condensate riser shall be insulated with 3/8” (9.5mm) Armaflex type insulation. The top of each riser shall be deeply swaged (3 in./76.2mm) to accept connection to the riser above/below, allowing for a floor to floor dimensional variance of ± one inch (25.4mm).  Units not having swaged riser-piping connections shall not be acceptable.  Couplings and trim pieces shall not be allowed.

Option: Type L riser piping.

Option: Unit mounted Thermostat provisions -- includes insulated junction box mounted inside discharge plenum that is connected to Molex-type connector wired to unit thermostat terminals, and having tile ring on cabinet for drywall installation to accept thermostat mounting. Use part number A9155724, A9155728 or A9155729 thermostat assembly, which is thermostat model ATM11C01, ATM11C03 or ATA11C04, respectively with mating Molex-type connector.

Fan and Motor Assembly:

The cabinet shall contain a removable motor/blower assembly. Units shall have a direct-drive centrifugal fan. The fan motor shall be 2-speed, permanently lubricated, PSC type with thermal overload protection. The fan motor shall be isolated from the fan housing by a torsionally flexible motor mounting system with rubber type grommets to inhibit vibration induced high noise levels associated with “hard wire belly band” motor mounting. Airflow/External static pressure rating of the unit shall be based on a wet coil and clean filter.

Option: High static motors.

Chassis:

The chassis, which incorporates the air coil, water coil, drain pan, and compressor, shall be easily installed for quick jobsite installation and future servicing purposes. The slide in chassis shall have an insulated panel separating the fan compartment from the compressor compartment. Compressors are not in the air stream. The chassis base shall be fabricated from heavy gauge galvanized steel formed to match the slide-in rails of the cabinet. All electrical connections between the chassis and cabinet shall be made via locking quick-connects. Units shall have a factory installed 1 inch (25.4mm) thick filter bracket and throwaway type glass fiber filter. Furnish one spare set of filters.

Water connections between chassis and the cabinet shall be accomplished via a hose kit consisting of Kevlar-reinforced EPDM core hose surrounded by a stainless-steel braid.  Hose kit shall have brass fittings with stainless-steel ferrules. Hose ends shall be solid External NPT which connects to mating fitting on cabinet shut off ball valve(s), and Internal NPSM (National Pipe Straight Mechanical) swivel end with fiber or EPDM washer which connects to mating threaded end connection on chassis. The hose kit shall be rated for 350 psi (2412 kPa) design working pressure.

Refrigerant Circuit:

Units shall have a sealed refrigerant circuit including a hermetic compressor, thermostatic expansion valve for refrigerant metering, an enhanced corrugated aluminum lanced fin and rifled copper tube refrigerant to air heat exchanger, a coaxial (tube in tube) refrigerant to water heat exchanger, and safety controls including a high pressure switch, low pressure switch (loss of charge), a high level condensate sensor, water coil low temperature sensor, and air coil low temperature sensor. Access fittings shall be factory installed on high and low pressure refrigerant lines to facilitate field service. Activation of any safety device shall prevent compressor operation via a microprocessor lockout circuit. The lockout shall be reset at the thermostat or disconnect switch.  Units that cannot be reset at the thermostat shall not be acceptable.

Hermetic compressors shall be internally sprung and externally isolated (with computer selected spring isolation).  Compressor shall have thermal overload protection.  Compressor shall be located in an insulated compartment away from air stream to minimize sound transmission.  All units (except units with rotary compressors) shall include a discharge muffler to further enhance sound attenuation.

Refrigerant to air heat exchangers shall utilize enhanced corrugated lanced aluminum fins and rifled copper tube construction rated to withstand 450 PSIG (3101 kPa) refrigerant working pressure.  Refrigerant to water heat exchangers shall be of copper inner water tube and steel refrigerant outer tube design, rated to withstand 450 PSIG (3101 kPa) working refrigerant pressure and 450 PSIG (3101 kPa) working water pressure.  The refrigerant to water heat exchanger shall be “electro-coated” with a low cure cathodic epoxy material a minimum of 0.4 mils thick (0.4 – 1.5 mils range) on all surfaces.  The black colored coating shall provide a minimum of 1000 hours salt spray protection per ASTM B117-97 on all external steel and copper tubing.  The material shall be formulated without the inclusion of any heavy metals and shall exhibit a pencil hardness of 2H (ASTM D3363-92A), crosshatch adhesion of 4B-5B (ASTM D3359-95), and impact resistance of 160 in-lbs (184 kg-cm) direct (ASTM D2794-93).

Refrigerant metering shall be accomplished by thermostatic expansion valve only. Expansion valves shall be dual port balanced types with external equalizer for optimum refrigerant metering.  Reversing valve shall be four-way solenoid activated refrigerant valve, which shall default to heating mode should the solenoid fail to function.  If the reversing valve solenoid defaults to cooling mode, an additional low temperature thermostat must be provided to prevent over-cooling an already cold room.

Option: The refrigerant to air heat exchanger shall be “electro-coated” with a low cure cathodic epoxy material a minimum of 0.4 mils thick (0.4 – 1.5 mils range) on all surfaces.  The black colored coating shall provide a minimum of 1000 hours salt spray protection per ASTM B117-97 on all galvanized end plates and copper tubing, and  a minimum of 2000 hours of salt spray on all aluminum fins.  The material shall be formulated without the inclusion of any heavy metals and shall exhibit a pencil hardness of 2H (ASTM D3363-92A), crosshatch adhesion of 4B-5B (ASTM D3359-95), and impact resistance of 160 in-lbs (184 kg-cm) direct (ASTM D2794-93).

Option:  The unit will be supplied with cupro nickel coaxial water to refrigerant heat exchanger.

Option:  The unit will be supplied with internally factory mounted two-way water valve for variable speed pumping requirements.  A factory-mounted or field-installed high pressure switch shall be installed in the water piping to disable compressor operation in the event water pressures build due to water freezing in the piping system.

Option:  The unit will be supplied with internally factory mounted automatic water flow regulators.

Option:  The unit will be supplied with internally mounted secondary pump for primary/secondary applications.

Cabinet Drain Pan:

The drain pan shall be constructed of galvanized steel and have a powder coat paint application to further inhibit corrosion. This corrosion protection system shall meet the stringent 1000 hour salt spray test per ASTM B117. If plastic type material is used, it must be HDPE (High Density Polyethylene) to avoid thermal cycling shock stress failure over the lifetime of the unit.  Stainless Steel materials are also acceptable.  Drain pan shall be fully insulated.  Drain pan shall have at a minimum a doubled sloped surface to allow positive drainage to the outlet opening, which shall be at the lowest level of the entire pan suface. Drain outlet shall be connected from pan outlet to condensate riser (if supplied) with factory installed trap inside of cabinet. The unit as standard will be supplied with solid-state electronic condensate overflow protection. Mechanical float switches will NOT be accepted.

Electrical:

A control box shall be located within the unit compressor compartment and shall contain a 50VA transformer, 24 volt activated, 2 or 3 pole compressor contactor, terminal block for thermostat wiring and solid-state controller for complete unit operation. Reversing valve and fan motor wiring shall be routed through this electronic controller. Units shall be name-plated for use with time delay fuses or HACR circuit breakers. Unit controls shall be 24 Volt and provide heating or cooling as required by the remote thermostat / sensor.

Option:  Disconnect Switch, Non-Fused

Option:  Circuit Breaker

Solid State Control System (CXM):

Units shall have a solid-state control system. Units utilizing electro-mechanical control shall not be acceptable. The control system microprocessor board shall be specifically designed to protect against building electrical system noise contamination, EMI, and RFI interference. The control system shall interface with a heat pump type thermostat. The control system shall have the following features:

- Anti-short cycle time delay on compressor operation.

- Random start on power up mode.

- Low voltage protection.

- High voltage protection.

- Unit shutdown on high or low refrigerant pressures.

- Unit shutdown on low water temperature.

- Condensate overflow electronic protection.

- Option to reset unit at thermostat or disconnect.

- Automatic intelligent reset.  Unit shall automatically reset the unit 5 minutes after trip if the fault has cleared. If a fault occurs 3 times sequentially without thermostat meeting temperature, then lockout requiring manual reset will occur.

- Ability to defeat time delays for servicing.

- Light emitting diode (LED) on circuit board to indicate high pressure, low pressure, low voltage, high voltage, low water/air temperature cut-out, condensate overflow, and control voltage status.

- The low-pressure switch shall not be monitored for the first 120 seconds after a compressor start command to prevent nuisance safety trips.

- 24V output to cycle a motorized water valve or other device with compressor contactor.

- Unit Performance Sentinel (UPS). The UPS warns when the heat pump is running inefficiently.

- Water coil low temperature sensing (selectable for water or anti-freeze).

- Air coil low temperature sensing.

NOTE: Units not providing the 8 safety protections of anti-short cycle, low voltage, high voltage, high refrigerant pressure, low pressure (loss of charge), air coil low temperature cut-out, water coil low temperature cut-out, and condensate overflow protections will not be accepted.

Option: Enhanced solid state control system (DXM)

This control system features two stage control of cooling and two stage control of heating modes for exacting temperature and dehumidification purposes.

This control system coupled with a multi-stage thermostat will better dehumidify room air by automatically running the heat pump’s fan at lower speed on the first stage of cooling thereby implementing low sensible heat ratio cooling. On the need for higher cooling performance the system will activate the second stage of cooling and automatically switch the fan to the higher fan speed setting.  This system may be further enhanced with a humidistat. Units not having automatic low sensible heat ratio cooling will not be accepted; as an alternate a hot gas reheat coil may be provided with control system for automatic activation.

Control shall have all of the above mentioned features of the CXM control system along with the following expanded features:

- Removable thermostat connector.

- Night setback control.

- Random start on return from night setback.

- Minimized reversing valve operation (Unit control logic shall only switch the reversing valve when cooling is demanded for the first time.  The reversing valve shall be held in this position until the first call for heating, ensuring quiet operation and increased valve life.).

- Override temperature control with 2-hour (adjustable) timer for room occupant to override setback temperature at the thermostat.

- Dry contact night setback output for digital night setback thermostats.

- Ability to work with heat pump or heat/cool (Y, W) type thermostats.

- Ability to work with heat pump thermostats using O or B reversing valve control.

- Emergency shutdown contacts.

- Boilerless system heat control at low loop water temperature.

- Ability to allow up to 3 units to be controlled by one thermostat.

- Relay to operate an external damper.

- Ability to automatically change fan speed from multistage thermostat.

- Relay to start system pump.

- 75 VA control transformer. Control transformer shall have load side short circuit and overload protection via a built in circuit breaker.

Remote Service Sentinel (CXM/DXM):

Solid state control system shall communicate with thermostat to display (at the thermostat) the unit status, fault status, and specific fault condition, as well as retrieve previously stored fault that caused unit shutdown. The Remote Service Sentinel allows building maintenance personnel or service personnel to diagnose unit from the wall thermostat.  The control board shall provide a signal to the thermostat fault light, indicating a lockout.  Upon cycling the G (fan) input 3 times within a 60 second time period, the fault light shall display the specific code as indicated by a sequence of flashes.  A detailed flashing code shall be provided at the thermostat LED to display unit status and specific fault status such as over/under voltage fault, high pressure fault, low pressure fault, low water temperature fault, condensate overflow fault, etc. Units that do not provide this remote service sentinel shall not be acceptable.

Option:  Lonworks interface system

Units shall have all the features listed above (either CXM or DXM) and the control board will be supplied with a LONWORKS interface board, which is LONMark certified. This will permit all units to be daisy chained via a 2-wire twisted pair shielded cable. The following points must be available at a central or remote computer location:

- space temperature

- leaving water temperature

- discharge air temperature

- command of space temperature setpoint

- cooling status

- heating status

- low temperature sensor alarm

- low pressure sensor alarm

- high pressure switch alarm

- condensate sensor alarm

- hi/low voltage alarm

- fan "ON/AUTO" position of space thermostat as specified above

- unoccupied / occupied command

- cooling command

- heating command

- fan "ON / AUTO" command

- fault reset command

- itemized fault code revealing reason for specific shutdown fault (any one of 7)

This option also provides the upgraded 75VA control transformer with load side short circuit and overload protection via a built in circuit breaker.

Option:  MPC (Multiple Protocol Control) interface system

Units shall have all the features listed above (either CXM or DXM) and the control board will be supplied with a Multiple Protocol interface board. Available protocols are BACnet MS/TP, Modbus, or Johnson Controls N2. The choice of protocol shall be field selectable/changeable via the use of a simple selector switch.  Protocol selection shall not require any additional programming or special external hardware or software tools. This will permit all units to be daisy chain connected by a 2-wire twisted pair shielded cable. The following points must be available at a central or remote computer location:

- space temperature

- leaving water temperature

- discharge air temperature

- command of space temperature setpoint

- cooling status

- heating status

- low temperature sensor alarm

- low pressure sensor alarm

- high pressure switch alarm

- condensate overflow alarm

- hi/low voltage alarm

- fan "ON/AUTO" position of space thermostat as specified above

- unoccupied / occupied command

- cooling command

- heating command

- fan "ON / AUTO" command

- fault reset command

- itemized fault code revealing reason for specific shutdown fault (any one of 7)

This option also provides the upgraded 75VA control transformer with load side short circuit and overload protection via a built in circuit breaker.

Return Panel / Supply Grilles:

The return panel shall be architecturally designed, acoustic type, flush mounted with hinged door for easy and quick access to filter and unit interior.  Chassis shall be easily removed.  The hinged return panel shall be made of heavy gauge die formed galvanized steel with a powder coat finish in “polar ice” color. Return air panels that protrude from wall more than 5/8 inch (15.9mm) are not acceptable.  Supply grille(s) shall be architecturally designed “brushed” aluminum or powder coated steel (color: polar ice).

Option:  supply grille with Double deflection damper style louvers.

Option: Style “H” Return air panel that allows outside air entry just behind panel on right or left side (Note: This option eliminates unit-mounted thermostat option).

Warranty:

Climate Master shall warranty equipment for a period of 12 months from start up or 18 months from shipping (which ever occurs first).

Option: Extended 4-year compressor warranty covers compressor for a total of 5 years.

Option: Extended 4-year refrigeration circuit warranty covers coils, reversing valve, expansion valve and compressor for a total of 5 years.

Option: Extended 4-year control board warranty covers the CXM/DXM control board for a total of 5 years.

# FIELD INSTALLED OPTIONS

Hose Kits - AHH Series (required for field water connections):

Water connections between chassis and the cabinet shall be accomplished via a hose kit consisting of Kevlar-reinforced EPDM core hose surrounded by a stainless-steel braid.  Hose kit shall have brass fittings with stainless-steel ferrules. Hose ends shall be solid External NPT which connects to mating fitting on cabinet shut off ball valve(s), and Internal NPSM (National Pipe Straight Mechanical) swivel end with fiber or EPDM washer which connects to mating threaded end connection on chassis. The hose kit shall be rated for 350 psi (2412 kPa) design working pressure.  This hose kit accessory is required for each cabinet.

Thermostats:

The thermostat shall be a ClimateMaster mechanical or electronic type thermostat as selected below with the described features:

a.	Single Stage Standard Manual Changeover (ATM11C01)

Thermostat shall be a single-stage, vertical mount, manual changeover with HEAT-OFF-COOL system switch and fan ON-AUTO switch. Thermostat shall have a mechanical temperature indicator and set point indication.  Thermostat shall only require 4 wires for connection.  Mercury bulb thermostats are not acceptable.

b.	Single Stage Digital Manual Changeover with Two-Speed Fan Control (ATM11C03) – DXM and PSC Fan required

Thermostat shall be a single-stage, digital, manual changeover with HEAT-OFF-COOL system switch, fan ON-AUTO switch, and fan LO-HI switch.  Thermostat shall have an LCD display with temperature and set-point(s) in ºF or ºC.  The Thermostat shall provide permanent memory of set-point(s) without batteries.  A fault LED shall be provided to display specific fault condition.  Thermostat shall come standard with remote temperature sensor, but may be operated with internal sensor if desired via installation of a jumper.

c.	Single Stage Digital Auto or Manual Changeover (ATA11U01)

Thermostat shall be a single-stage, digital, auto or manual changeover with HEAT-OFF-COOL-AUTO system switch and fan ON-AUTO switch. Thermostat shall have an LCD display with temperature and set-point(s) in ºF or ºC.  The Thermostat shall provide permanent memory of set-point(s) without batteries.  A fault LED shall be provided to display specific fault condition. Thermostat shall provide temperature display offset for custom applications.

d.	Single Stage Digital Automatic Changeover with Two-Speed Fan Control (ATA11C04) – DXM and PSC Fan required

Thermostat shall be a single-stage, digital, auto or manual changeover with HEAT-OFF-COOL-AUTO system switch, fan ON-AUTO switch, and fan LO-HI switch.  Thermostat shall have an LCD display with temperature and set-point(s) in ºF or ºC.  The Thermostat shall provide permanent memory of set-point(s) without batteries.  A fault LED shall be provided to display specific fault condition.  Thermostat shall come standard with remote temperature sensor, but may be operated with internal sensor if desired via installation of a jumper.

e.	Multistage Digital Automatic Changeover (ATA22U01)

Thermostat shall be multi-stage (2H/2C), manual or automatic changeover with HEAT-OFF-COOL-AUTO system settings and fan ON-AUTO settings.  Thermostat shall have an LCD display with temperature, set-point(s), mode, and status indication.  The temperature indication shall be selectable for ºF or ºC.  The thermostat shall provide permanent memory of set-point(s) without batteries.  A fault LED shall be provided to indicate specific fault condition(s).  Thermostat shall provide temperature display offset for custom applications. Thermostat shall allow unit to provide better dehumidification with optional DXM controller by automatically using lower fan speed on stage 1 cooling (higher latent cooling) as main cooling mode, and automatically shifting to high speed fan on stage 2 cooling.

f.	Single Stage Manual Changeover Programmable 5/2 Day (ATP11N01)

Thermostat shall be 5 day/2 day programmable (with up to 4 set points per day), single stage (1H/1C), manual changeover with HEAT-OFF-COOL system settings and fan ON-AUTO settings.  Thermostat shall have an LCD display with temperature, set-point(s), mode, and status indication.  The temperature indication shall be selectable for ºF or ºC.  The thermostat shall provide permanent memory of set-point(s) without batteries.  Thermostat shall provide convenient override feature to temporarily change set point.

g.	Multistage Automatic or Manual Changeover Programmable 5/2 Day (ATP21U01)

Thermostat shall be 5 day/2 day programmable (with up to 4 set points per day), multi-stage (2H/1C), automatic or manual changeover with HEAT-OFF-COOL-AUTO system settings and fan ON-AUTO settings.  Thermostat shall have an LCD display with temperature, set-point(s), mode, and status indication.  The temperature indication shall be selectable for ºF or ºC.  The thermostat shall provide permanent memory of set-point(s) without batteries.  Thermostat shall provide convenient override feature to temporarily change set point.

h.	Multistage Automatic or Manual Changeover Programmable 7 Day (ATP32U01)

Thermostat shall be 7 day programmable (with up to 4 set points per day), multi-stage (3H/2C), automatic or manual changeover with HEAT-OFF-COOL-AUTO system settings and fan ON-AUTO settings.  Thermostat shall have a blue backlit dot matrix LCD display with temperature, set-points, mode, and status indication.  The temperature indication shall be selectable for ºF or ºC.  Time display shall be selectable for 12 or 24 hour clock.  Fault identification shall be provided (when used with ClimateMaster CXM or DXM controls) to simplify troubleshooting by providing specific unit fault at the thermostat with red backlit LCD during unit lockout.  The thermostat shall provide permanent memory of set-points without batteries.  Thermostat shall provide heating set-point range limit, cooling set-point range limit, temperature display offset, keypad lockout, dead-band range setting, and inter-stage differential settings.  Thermostat shall provide progressive recovery to anticipate time required to bring space temperature to the next programmed event.  Thermostat shall provide an installer setup for configuring options and for setup of servicing contractor name and contact information.  Thermostat shall allow the use of an accessory remote and/or outdoor temperature sensor (AST008).  Thermostat navigation shall be accomplished via five buttons (up/down/right/left/select) with menu-driven selections for ease of use and programming.

i.	Multistage Automatic or Manual Changeover Programmable 7 Day with Humidity Control (ATP32U02)

Thermostat shall be 7 day programmable (with up to 4 set points per day), multi-stage (3H/2C), automatic or manual changeover with HEAT-OFF-COOL-AUTO system settings and fan ON-AUTO settings.  Separate dehumidification and humidification set points shall be configurable for discreet outputs to a dehumidification option and/or an external humidifier. Installer configuration mode shall allow thermostat dehumidification mode to operate with ClimaDry reheat or with ECM fan dehumidification mode via settings changes.  Thermostat shall have a blue backlit dot matrix LCD display with temperature, relative humidity, set-points, mode, and status indication.  The temperature indication shall be selectable for ºF or ºC.  Time display shall be selectable for 12 or 24 hour clock.  Fault identification shall be provided (when used with ClimateMaster CXM or DXM controls) to simplify troubleshooting by providing specific unit fault at the thermostat with red backlit LCD during unit lockout.  The thermostat shall provide permanent memory of set-points without batteries.  Thermostat shall provide heating set-point range limit, cooling set-point range limit, temperature display offset, keypad lockout, dead-band range setting, and inter-stage differential settings.  Thermostat shall provide progressive recovery to anticipate time required to bring space temperature to the next programmed event.  Thermostat shall provide an installer setup for configuring options and for setup of servicing contractor name and contact information.  Thermostat shall allow the use of an accessory remote and/or outdoor temperature sensor (AST008).  Thermostat navigation shall be accomplished via five buttons (up/down/right/left/select) with menu-driven selections for ease of use and programming.

DDC Sensors:

ClimateMaster wall mounted DDC sensor to monitor room temperature and interfaces with optional interface system described above. Several types as described below:

- Sensor only with no display (LON and MPC).

- Sensor with override (LON only).

- Sensor with setpoint and adjustment override (MPC only).

- Sensor with setpoint and adjustment override, LCD display, status/fault indication (LON and MPC).