# GENERAL

Furnish and install ClimateMaster SWT large water-source heat pumps as indicated on the plans.

Equipment shall be completely assembled, piped and internally wired. Capacities and characteristics as listed in the schedule and the specifications that follow.

Units shall be supplied completely factory built capable of operating over an entering water temperature range from 30° to 120°F (-1.1° to 48.9°C) as standard. All equipment listed in this section must be rated in accordance with Air-Conditioning, Heating and Refrigeration Institute/International Standards Organization (AHRI/ISO 13256-2). All equipment must be tested, investigated, and determined to comply with the requirements of

the standards for Heating and Cooling Equipment UL 60335-2-40 4th Edition, UL 60335-1 6th Edition for the United States and Can/CSA C22.2 No. 60335-

2-40:22, CAN/CSA C22.2 No 60335-1:16 for Canada,

by Intertek Testing Laboratories (ETL). The units shall have ETL-US-C labels.

All units shall pass a factory acceptance test. The quality control system shall automatically perform the factory acceptance test via computer. NOTE: If unit fails the factory acceptance test it shall not be allowed to ship.

# BASIC CONSTRUCTION

All units must have multiple removable panels for serviceability of compressor compartment.

Units having only one access panel shall not be acceptable. All units must have front access for side-by-side installations.

The heat pumps shall be fabricated from heavy gauge galvanized steel. All interior surfaces shall be lined with 1/2-inch (12.7 mm) thick, 11/2 lb/ft3 (24 kg/ m3) acoustic type glass fiber insulation. Insulation placement shall be designed in a manner that will eliminate any exposed edges.

Standard cabinet panel insulation must meet NFPA 90A requirements, air erosion and mold growth limits of UL-181, stringent fungal resistance test per ASTM-C1071 and ASTM G21, and shall meet zero-level bacteria growth per ASTM G22. Unit insulation must meet these stringent requirements or unit(s) will not be accepted.

Cabinets shall have separate holes and knockouts for entrance of line voltage and low voltage control wiring. All factory-installed wiring passing through factory knockouts and openings shall be protected

from sheet metal edges at openings by plastic ferrules. Supply and return water connections shall be steel grooved fittings. Contractor shall be responsible for any extra costs involved in the installation of units that do not have this feature. Contractor must ensure that units can be easily removed for servicing and coordinate locations of electrical conduit and lights with the electrical contractor.

Option: Compressor Blankets shall be factory installed on each compressor.

# REFRIGERANT CIRCUIT

Units shall have sealed, isolated refrigerant circuit(s), each including a high-efficiency scroll compressor designed for heat pump operation, a electronic expansion valve for precise refrigerant metering,

a reversing valve, load and source brazed-plate refrigerant-to-water heat exchangers, and safety controls including a high pressure switch, discharge and suction pressure transducers, water flow proving sensor, and low fluid temperature sensors. Access fittings shall be factory installed on high and low pressure refrigerant lines to facilitate field service. Activation of any safety device shall prevent compressor operation via a microprocessor lockout circuit.

Unit shall be supplied with extended range insulation, which adds closed cell insulation to internal water lines, and provides insulation on suction side refrigeration tubing including refrigerant-to-water heat exchangers.

Hermetic compressors shall be internally sprung. The compressors shall have a vibration isolation system. The compressors will be mounted on specially engineered sound-tested EPDM vibration isolation grommets to a large heavy gauge cabinet divider panel. Compressors shall have thermal overload protection.

The refrigerant-to-water heat exchangers shall be stainless steel-copper brazed plate, rated to withstand 650 PSIG (4,482 kPa) working refrigerant pressure and 300 PSIG (2,068.4 kPa) working water pressure.

ClimateMaster works continually to improve its products. As a result, the design and specifications of each product at the time of order may be changed without notice and may not be as described herein. Please contact ClimateMaster’s Customer Service Department at 800-299-9747 for specific information on the current design and specifications. Statements and other information contained herein are not express warranties and do not form the basis of any bargain between the parties, but are merely ClimateMaster’s opinion or commendation of its products. The latest version of this document is available at www.climatemaster.com.

Engineered and assembled in the USA. © ClimateMaster, Inc. All Rights Reserved 2024

All units shall be supplied with a Refrigerant Detection System (RDS) with sensors strategically placed within the cabinet. In the event of a refrigerant leak, the RDS disables compressor operation and the RDS control board sends a signal the control to energize a pair of contacts to control a ventilation fan, if required. Units charged with 62 ounces or greater of R-454B that do not have an RDS shall not be acceptable.

Option: Units shall be supplied with factory installed pressure relief valves that will open at

625 PSIG. The valves shall be provided to route (field connected) refrigerant out of the building in the event of a fire, or other high pressure situation.

# ELECTRICAL

A control box shall be located within the unit compressor compartment and shall contain a transformer, 24V activated, 3-pole compressor contactor, terminal block for communication wiring and solid-state controller for complete unit operation. Reversing valve wiring shall be routed through this electronic controller. Units shall be name-plated for use with time delay fuses or HACR circuit breakers. Unit controls shall be 24V and provide heating or cooling

as required by the desired application. Units shall have a solid-state time delay relay and random start to prevent both compressors from starting simultaneously.

# OPTICORE COMMUNICATING CONTROL

Units shall have a solid-state control system. Units utilizing electro-mechanical control shall not be acceptable. The control system microprocessor board shall be specifically designed to protect against building electrical system noise contamination, EMI, and RFI interference.

This control system is a communicating controller with the following features:

- 28 universal inputs.

- 16 universal outputs.

- 4.3” touchscreen interface (HMI).

- Anti-short cycle time delay on compressor operation.

- Random start on power up mode.

- BMS integration via BACnet MS/TP, Modbus, or ARC156.

- Electronic Expansion Valve (EEV) control.

- Low-voltage protection.

- Phase monitoring.

- High-voltage protection.

- Unit shutdown on high or low refrigerant pressures.

- Unit shutdown on low water temperature.

- Automatic intelligent reset. Unit shall automatically reset the unit 5 minutes after trip if the fault has cleared. If a fault occurs 3 times sequentially without thermostat meeting temperature, then lockout requiring manual reset will occur.

- Ability to defeat time delays for servicing.

- Thermal dispersion flow sensor

- Emergency shutdown contacts.

- Entering and leaving water temperature sensing.

- Compressor discharge and suction temperature sensing.

- 75VA control transformer. Control transformer shall have load side short circuit and overload protection via a built-in circuit breaker.

NOTE: Units not providing the five safety protections of anti-short cycle, low voltage, high voltage, and high refrigerant pressure cut-out will not be accepted.

# WARRANTY

ClimateMaster shall warranty equipment for a period of 12 months from startup or 18 months from shipping (whichever occurs first).

Option: Extended 4-year compressor warranty covers compressor for a total of 5 years.

Option:	Extended 4-year refrigeration circuit warranty covers coils, reversing valve, expansion valve and compressor for a total of 5 years.

Option: Extended 4-year control board warranty covers the factory-supplied controls for a total of 5 years.

ClimateMaster works continually to improve its products. As a result, the design and specifications of each product at the time of order may be changed without notice and may not be as described herein. Please contact ClimateMaster’s Customer Service Department at 800-299-9747 for specific information on the current design and specifications. Statements and other information contained herein are not express warranties and do not form the basis of any bargain between the parties, but are merely ClimateMaster’s opinion or commendation of its products. The latest version of this document is available at www.climatemaster.com.

Engineered and assembled in the USA. © ClimateMaster, Inc. All Rights Reserved 2024

# FIELD-INSTALLED OPTIONS

Piping Adapters

Units shall be supplied with full-set of four (4) grooved to MPT piping adapters to facilitate connection to the building loop. These are available in 2” and 2.5” diameters.

Hose Kits

All units shall be connected with hoses. The hoses shall be 2-feet (61 cm) long, braided stainless steel; fire-rated hoses complete with adapters. Only fire-rated hoses will be accepted.

Strainers

The following strainers are field obtained and installed.

- 3-inch FPT Y-strainer. 20-40 mesh screen.

- 3-inch FPT Basket strainer. 20-40 mesh screen.

ATTENTION

This product specification document is furnished as a means to copy and paste ClimateMaster product information into project specification. It is not intended to be a complete list of product requirements. This document is an excerpt from the product submittal and must not be used without consulting the complete product submittal. For complete product installation and application requirements, please consult the complete product submittal. ClimateMaster is not responsible for misuse of this document or a failure to adequately review specific requirements in the product catalog.

ClimateMaster works continually to improve its products. As a result, the design and specifications of each product at the time of order may be changed without notice and may not be as described herein. Please contact ClimateMaster’s Customer Service Department at 800-299-9747 for specific information on the current design and specifications. Statements and other information contained herein are not express warranties and do not form the basis of any bargain between the parties, but are merely ClimateMaster’s opinion or commendation of its products. The latest version of this document is available at www.climatemaster.com.

Engineered and assembled in the USA. © ClimateMaster, Inc. All Rights Reserved 2024