## TST_Faults
# | Fault Description | Possible cause 1 | Possible cause 2 | Possible cause 3 | Possible cause 4 | Possible cause 5 | Possible cause 6 | Possible cause 7 | Possible cause 8
0 | None | None
1 | No Fault | None
2 | High Discharge Pressure | Dirty Air Filter - Heating | Low Airflow - Heating | Low Water Flow - Cooling | Low Water Flow - Domestic Hot Water | Overcharged | Faulty Discharge Pressure Transducer
3 | Low Suction Pressure | Low Refrigerant Charge | Faulty Expansion Valve | Incorrect Loop Configuration | Dirty Air Filter - Cooling | Low Airflow - Cooling | Low Water Flow - Heating or Domestic Hot Water | Faulty Suction Pressure Transducer | Faulty Check Valve
4 | Invalid | No fault assigned to code 4
5 | Invalid | No fault assigned to code 5
6 | Condensate Overflow | Blocked Drain | Moisture on Sensor | Poor Drainage | Clogged Air Filter | Restricted Return Airflow
7 | Over / Under Voltage | Voltage Too High | Voltage Too Low
8 | Invalid | No fault assigned to code 8
9 | Invalid | No fault assigned to code 9
10 | ECM Low RPM | Blower not configured properly | Incorrect Blower | Blower Wiring Issue | Blower Power Issue
11 | Low Air Coil Pressure | Low Return Air Temperature | Clogged Air Filter | Faulty Suction Pressure Transducer | Insufficient Charge
12 | Control Fault | EXM not properly programmed | Faulty EXM
13 | Low Pump Flow | Air-locked Pump | Pump Failure | Faulty Flow Sensor | Incorrect System Setup (single instead of parallel)
14 | High Discharge Temperature | Insufficient Charge | Water Temp out of Range | Air Temp out of Range | Fouled Heat Exchanger | Faulty Expansion Valve
15 | Discharge Pressure Sensor | Faulty Wiring | Faulty Transducer | Faulty EXM
16 | Suction Pressure Sensor | Faulty Wiring | Faulty Transducer | Faulty EXM
17 | Space Temperature Sensor | Thermostat Wiring Issue | Incorrect Master/Slave setting | Faulty Thermostat | Faulty EXM
18 | Space Humidity Sensor | Thermostat Wiring Issue | Incorrect Master/Slave setting | Faulty Thermostat | Faulty EXM
19 | Low Refrig Pressure Differential | Stuck Reversing Valve | Faulty Compressor
20 | ECM Configuration | Incorrect Unit Configuration | Incorrect Motor size
21 | High Blower Static | Clogged Air Filter | Faulty Ductwork
22 | Grundfos Flow Sensor | Sensor Wiring Issue | Faulty Flow (VFD) Sensor | Faulty EXM
23 | Grundfos Pressure Sensor | Sensor Wiring Issue | Faulty Pressure (DPD) Sensor | Faulty EXM
24 | Leaving Air Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
25 | High EWT warning | High Loop Temperature
26 | Low EWT warning | Low Loop Temperature
27 | Cabinet Temperature Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
28 | No Loop Pump Feedback | No Line Voltage | Faulty wiring | Faulty EXM
29 | Low Loop Pump Voltage warning | Low Supply Voltage
30 | Loop Pump Locked Rotor fault | Contaminants in Impeller | Seized Impeller
31 | Loop Pump Voltage Shutdown fault | Low Supply Voltage
32 | Loop Pump Sensor fault | Faulty RPM Sensor
33 | No DHW Pump Feedback warning | No Line Voltage | Faulty wiring | Faulty EXM
34 | Low DHW Pump Voltage warning | Low Supply Voltage
35 | DHW Pump Locked Rotor fault | Contaminants in Impeller | Seized Impeller
36 | DHW Pump Voltage Shutdown fault | Low Supply Voltage
37 | DHW Pump Sensor fault | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
38 | Suction Temperature Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
39 | Discharge Temperature Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
40 | Entering HW Temperature Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
41 | Leaving HW Temperature Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
42 | Air Coil Liquid Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
43 | Air Coil Vapor Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
44 | Water Coil Vapor Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
45 | Water Coil Liquid Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
46 | HW HX Liquid Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
47 | Spare T1 Temperature Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty EXM
48 | Lower HW Tank Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty WXM
49 | Upper HW Tank Temp Sensor | Sensor Wiring Issue | Faulty Thermistor | Faulty WXM
50 | Reduced HW setpoint warning | High Discharge Temperature | High Discharge Pressure | Fouled Heat Exchanger
51 | High Suction Pressure warning | Dirty Filter - Heating | Low Airflow - Heating | Low Water Flow - Cooling | Low Water Flow - Water Heating | Overcharged | Faulty Pressure Transducer
52 | Low Suction Pressure warning | Insufficient Charge | Faulty Expansion Valve | Incorrect Loop Configuration | Dirty Filter - Cooling | Low Airflow - Cooling | Low Water Flow - Heating or Domestic Hot Water | Faulty Pressure Transducer | Faulty Check Valve
53 | Low Discharge Pressure warning | Low Entering Water Temperature | Low Entering Air Temperature
54 | Loss of WXM Communications | Faulty wiring from EXM to WXM | Faulty WXM | Faulty EXM | Incorrect Master/Slave setting
55 | WXM High Temperature warning | Elements Thermostat set too High
56 | HW HX Performance | Fouled HW Heat Exchanger
57 | Low Discharge Superheat | Faulty Expansion valve | Faulty Discharge Pressure transducer | Faulty Discharge Temperature sensor | Improperly installed Discharge Temperature sensor
58 | Low Suction Superheat | Faulty Expansion valve | Faulty Suction Pressure transducer | Faulty Suction Temperature sensor | Improperly installed Suction Temperature sensor
59 | High Suction Superheat | Faulty Expansion valve | Faulty Suction Pressure transducer | Faulty Suction Temperature sensor | Improperly installed Suction Temperature sensor | Insufficient charge | Faulty Check valve
60 | General Compressor fault | Check compressor sub-faults (61-71 & 75 & 76)
61 | High Temperature Shutdown | Improper contact with Heat sink | Damaged Inverter thermistor
62 | High Current at Start Up | Low Input Voltage | Incorrect Compressor wiring | Faulty Compressor | Damaged Inverter board | Incorrect Inverter board
63 | High Current Shutdown | Low Input Voltage | Incorrect Compressor wiring | Faulty Compressor | Damaged Inverter board | Incorrect Inverter board
64 | High DC Voltage Shutdown | High input voltage | Damaged Inverter board
65 | Current Sensor Warning | Damaged Inverter board
66 | Heat Sink Thermistor Error | Damaged Inverter board
67 | Current Sensor Error | Damaged Inverter board
68 | Lack of Inverter COMM / Initialization | Faulty Wiring From MIM to Board | Faulty MIM | Damaged Inverter board
69 | Low Voltage Shutdown - Inverter | Low Input Voltage | Damaged Inverter board | Faulty wiring to Compressor | Faulty wiring between Inverter and MIM
70 | Power Supply Sync Warning | Check Input Voltage
71 | Converter Over Current Shutdown | Low Input Voltage
72 | Protect Operation - Comp Current | High Load Condition | Faulty Compressor | Incorrect Inverter board | Damaged Inverter board
73 | Protect Operation - Heat Sink Temp | Improper contact with Heat sink
74 | Protect Operation - Input Current | High Load Condition | Low Input Voltage | Water temp at range limit | Air temp at range limit
75 | Lack of MIM Communications | Faulty wiring from EXM to MIM | Faulty MIM | Faulty EXM
76 | Low Voltage Shutdown | Low input voltage | Incorrectly selected transformer tap
77 | Low Leaving Air Temperature | Low Entering Air Temperature | Faulty Thermistor | Incorrectly installed leaving air temperature sensor | Check unit capacity | Incorrect airflow
78 | High Leaving Air Temperature | High Entering Air Temperature | Faulty Thermistor | Incorrectly installed leaving air temperature sensor | Check unit capacity | Incorrect airflow
79 | Low Subcooling | Low unit charge
80 | ECM Blower Motor fault | Check ECM sub-faults (81-86)
81 | ECM Lost Rotor fault | Blower wheel set screw loose | Blower wheel dragging | Blower wheel locked
82 | ECM Current Trip fault | Low input voltage | Faulty ECM
83 | ECM Temperature Limit fault | High ambient motor temperature | Dirty motor housing
84 | ECM Locked Rotor fault | Debris in blower assembly | Blower wheel dragging | Faulty motor bearing
85 | ECM Over Voltage fault | High input voltage | Faulty ECM
86 | ECM Under Voltage fault | Low input voltage | Power cable | Faulty ECM
87 | ECM Blocked Inlet fault | Low input voltage | Clogged Air Filter | Dirty air coil | External static is too high
88 | ECM Power Limit warning | Low input voltage | Clogged Air Filter | Dirty air coil | External static is too high
89 | ECM Temperature Limit warning | High ambient motor temperature | Dirty motor housing
90 | ECM No Communications fault | Faulty wiring from EXM to ECM | Faulty ECM | Faulty EXM | No input voltage
91 | ECM Horsepower Configuration fault | Incorrect motor | Incorrect unit configuration
92 | ECM Bad Parameter fault | Incorrect motor | Incorrect unit configuration
93 | Heating check valve | Leaking heating check valve | Leaking EEV 1
94 | Cooling check valve | Leaking cooling check valve | Leaking EEV 2
95 | HW check valve | Leaking HW check valve
96 | Low HW Delta-T warning | Run HW Check mode | Faulty entering HW temperature sensor | Improperly installed entering HW temperature sensor | Faulty leaving HW temperature sensor | Improperly installed leaving HW temperature sensor
97 | Pressure Sensor Calibration fault | Unit not equalized | Faulty discharge pressure transducer | Faulty suction pressure transducer
98 | Loop Flow w/o Loop Pump warning | Loop pump check valve stuck open
99 | Excessive Transition Mode operation | Stuck Reversing Valve | Faulty Compressor
100 | Low Loop Pressure warning | Low Loop Pressure | Improperly installed Pressure (DPD) Sensor | Faulty Pressure (DPD) Sensor
101 | None | None
102 | None | None
103 | None | None
104 | None | None
105 | None | None
106 | None | None
107 | None | None
108 | None | None
109 | None | None
110 | None | None
111 | None | None
112 | None | None
113 | None | None
114 | None | None
115 | None | None
116 | None | None
117 | None | None
118 | None | None
119 | None | None
120 | None | None
121 | None | None
122 | None | None
123 | None | None
124 | None | None
125 | None | None
126 | None | None
127 | None | None
128 | None | None
129 | None | None
130 | None | None
131 | None | None
132 | None | None
133 | None | None
134 | None | None
135 | None | None
136 | None | None
137 | None | None
138 | None | None
139 | None | None
140 | None | None
141 | None | None
142 | None | None
143 | None | None
144 | None | None
145 | None | None
146 | None | None
147 | None | None
148 | None | None
149 | None | None
150 | None | None
151 | None | None
152 | None | None
153 | None | None
154 | None | None
155 | None | None
156 | None | None
157 | None | None
158 | None | None
159 | None | None
160 | None | None
161 | None | None
162 | None | None
163 | None | None
164 | None | None
165 | None | None
166 | None | None
167 | None | None
168 | None | None
169 | None | None
170 | None | None
171 | None | None
172 | None | None
173 | None | None
174 | None | None
175 | None | None
176 | None | None
177 | None | None
178 | None | None
179 | None | None
180 | None | None
181 | None | None
182 | None | None
183 | None | None
184 | None | None
185 | None | None
186 | None | None
187 | None | None
188 | None | None
189 | None | None
190 | None | None
191 | None | None
192 | None | None
193 | None | None
194 | None | None
195 | None | None
196 | None | None
197 | None | None
198 | None | None
199 | None | None
200 | No Zone Damper Power | Bad Input Voltage | Bad Damper Power Wiring
201 | Thermostat Configuration Error | ZXM Detected with Thermostat | Incorrect Thermostat Wiring at EXM
202 | Loss of Thermostat Communications | Bad Wiring from ZXM to Thermostat | Bad Thermostat | Bad ZXM Control
203 | Loss of ZXM Communications | Bad Wiring from ZXM to EXM | Bad EXM Control | Bad ZXM Control
204 | Loss of EXM Communications | Bad Wiring from ZXM to EXM | Bad EXM Control | Bad ZXM Control
205 | ZXM Configuration Error | Multiple ZXMs Detected at EXM | Incorrect ZXM Wiring at EXM