NOTICE!

# ClimateMaster

# TRANQUILITY® ROOFTOP “TRT” 036-072 60 Hz

# ENGINEERING SPECIFICATIONS

Revised: November 11, 2021

General:

Furnish and install ClimateMaster Tranquility® “TRT” Rooftop Water Source Heat Pumps, as indicated on the plans. Equipment shall be completely assembled, piped and internally wired. Capacities and characteristics as listed in the schedule and the specifications that follow.

Units shall be supplied completely factory built capable of operating over an entering water temperature range from 20° to 120°F (-6.7° to 48.9°C) as standard. All equipment listed in this section must be rated and certified in accordance with Air-Conditioning, Heating and Refrigeration Institute/International Standards Organization (AHRI/ISO 13256-1). All equipment must be tested, investigated, and determined to comply with the requirements of the standards for Heating and Cooling Equipment UL-1995 for the United States and CAN/CSA-C22.2 NO.236 for Canada, by Intertek Testing Laboratories (ETL). The units shall have AHRI/ISO and ETL-US-C labels.

All units shall pass a factory acceptance test. The quality control system shall automatically perform factory acceptance test via computer. A detailed report from the factory acceptance test shall ship with each unit. (Note: If unit fails the factory acceptance test, it shall not be allowed to ship. Unit serial number shall be recorded by factory acceptance test and furnished on report card for ease of unit warranty status.)

Basic Construction:

Units shall be designed for outdoor installation and usage and shall be ETL or UL tested to withstand UL rain test standards.

All exterior and other painted surfaces shall be constructed of galvanized steel finished with both sides having powder paint coated surfaces. This corrosion protection system shall meet the stringent 1,000-hour salt spray test per ASTM B117.

Roof shall be constructed of single piece of steel as described above (except on largest of unit sizes in which case shall be a maximum of two pieces joined by a standing seam construction). All roof edges shall overlap sides of unit and have a 45º lip extending away from unit sides so that rainwater drippage shall not fall on top of access doors.

Access to filters, indoor blower, electrical controls, compressor compartment, and damper section shall be provided by double wall construction for access doors and noncorrosive hardware.

The compressor and electrical control compartment shall be isolated from the system air streams.

Bottom base pan of entire unit shall have no penetrations by bolts or screws. All base pan edges and any openings shall contain 1 inch upturns at all edges and shall be sealed with silicone caulking to prevent water from dripping through base pan.

All interior surfaces shall be lined with 1 inch (25.4 mm) thick, 1-1/2 lb/ft3 (24 kg/m3) acoustic type glass fiber insulation. Insulation placement shall be designed in a manner that will eliminate any exposed edges to prevent the introduction of glass fibers into the air stream. All air handling compartments shall utilize foil-faced insulation for ease of cleaning.

Standard cabinet panel insulation must meet NFPA 90A requirements, air erosion and mold growth limits of UL-181, stringent fungal resistance test per ASTM-C1071 and ASTM G21, and shall meet zero level bacteria growth per ASTM G22. Unit insulation must meet these stringent requirements or unit(s) will not be accepted.

Entire unit base shall be insulated on the underneath side to provide condensation protection and noise attenuation. The unit shall be furnished with 2 inch (50 mm) filter rails and one set 2 inch (50 mm) throwaway filters. Filter rails shall be field convertible without the need for additional parts to accept 4 inch filters.

Option: Unit shall be furnished with factory-installed 2 inch (50 mm) pleated filters.

Option: Unit shall be furnished with factory-configured 4 inch (100 mm) filter rails and 4 inch

(100 mm) pleated filters.

Option: The unit shall be supplied with internally mounted secondary pump for primary/secondary 	applications, including one pipe systems.

Fan and Motor Assembly:

The assembly shall include a fan, housing and solid steel fan shaft encased in ball bearings. Unit shall have a belt drive fan assembly, fan pulley and adjustable motor sheave with V-belt drive. Fan shall be forward curved, low speed centrifugal that has been statically and dynamically balanced, and tested in accordance with current A.M.C.A. standards bulletin 210. Fan bearings shall be permanently lubricated type and be self-aligning. The motor shall be a single or three-phase, high efficiency, ball bearing, open type with internal thermal overload protection. The motor shall be mounted on an adjustable base for proper belt tension. The fan and motor assembly must be capable of overcoming the external static pressures up to and including as shown in the unit submittal. Airflow/Static pressure rating of the unit shall be based on a wet coil and a clean filter in place. Fan and motor assembly will be mounted on an easily removable slide out assembly with safety stop for easy access and maintenance; motor shall be factory wired with wire of sufficient length to allow fan/motor assembly to be removed from unit and be placed on roof of unit for servicing.

Variable Frequency Drives (VFD). VFD controls shall be factory mounted, installed, and programmed. VFD have the capability to reduce airflow down to 60% of maximum airflow. Products not containing factory mounted VFD controls shall not be acceptable.

Refrigerant Circuit:

Units shall use EarthPure® (HFC-410A) refrigerant only. Units shall have a sealed refrigerant circuit including a high efficiency two-stage scroll compressor designed for heat pump operation, a dual port balanced thermostatic expansion valve for refrigerant metering, a filter dryer, an enhanced corrugated finned tube refrigerant to air heat exchanger, a reversing valve, a coaxial (tube in tube) refrigerant to water heat exchanger, and safety controls including a high pressure switch, low pressure switch (loss of charge), water coil low temperature sensor, and air coil low temperature sensor. Both high and low pressure switches shall be installed on Schrader fittings for service or replacement without having to evacuate and recharge refrigerant. Access fittings shall also be factory installed on high and low-pressure refrigerant lines to facilitate field service. Suction line shall be insulated to prevent condensation. Activation of any safety device shall prevent compressor operation via a microprocessor board lockout circuit. The lockout circuit shall be reset at the thermostat or at the disconnect switch. Units that cannot be reset at the thermostat shall not be acceptable.

The 2-stage scroll compressor(s) will be mounted on external grommets specifically selected for maximized vibration attenuation. Compressor shall be mounted on a double isolation compressor deck, so as to further reduce vibration transmission to unit base. Compressor shall have thermal overload protection and be located in an insulated compartment away from air stream to minimize sound transmission.

Refrigerant to air heat exchangers shall utilize enhanced corrugated lanced aluminum fins and rifled copper tube construction rated to withstand 650 PSIG (4481 kPa) refrigerant working pressure. Refrigerant to water heat exchangers shall be of copper inner water tube that is deeply fluted, and steel refrigerant outer tube co-axial design, rated to withstand 650 PSIG (4481 kPa) working refrigerant pressure and 650 PSIG (4481 kPa) working water pressure. The refrigerant to water heat exchanger shall be “electro-coated” with a low cure cathodic epoxy material a minimum of 0.4 mils thick (0.4 – 1.5 mils range) on all surfaces. The black colored coating shall provide a minimum of 1,000 hours salt spray protection per ASTM B117-97 on all external steel and copper tubing. The material shall be formulated without the inclusion of any heavy metals and shall exhibit a pencil hardness of 2H (ASTM D3363-92A), crosshatch adhesion of 4B-5B (ASTM D3359-95), and impact resistance of 160 in-lbs (184 kg-cm) direct (ASTM D2794-93).

Refrigerant metering shall be accomplished by thermostatic expansion valve only. Expansion valves shall be dual port balanced type with external equalizer for optimum refrigerant metering. Units shall be designed and tested for operating ranges of entering water temperatures from 20° to 120°F (-6.7° to 48.9°C). Reversing valve shall be four-way solenoid activated refrigerant valve, which shall default to heating mode should the solenoid fail to function. If the reversing valve solenoid defaults to cooling mode, an additional low temperature thermostat must be provided to prevent over-cooling an already cold room.

Option: The unit will be supplied with cupro-nickel coaxial water to refrigerant heat exchanger.

Option: The unit will be supplied with internally factory mounted two-way water valve with end switch for variable speed pumping requirements. A factory-mounted or field-installed high pressure switch shall be installed in the water piping to disable compressor operation in the event water pressures build due to water freezing in the piping system.

Option: Unit shall include ClimaDry® II reheat option. Only modulating reheat that will adjust capacity based upon supply air temperature to provide “neutral” (72ºF, 22.2ºC) constant air temperature will be accepted. “Neutral” supply air temperature shall be provided regardless of entering loop water temperatures or refrigerant condensing pressures. Control of reheat must be accomplished via a humidistat or dehumidistat contact closure. Refrigerant circuit must be AHRI certified. Approved equal manufacturers may provide pre-engineered integrated modulating hot gas reheat within the unit cabinet. Any design costs and costs of field installed items shall be borne by mechanical contractor. Refrigerant circuits that are not AHRI certified when the reheat option is applied will not be accepted. (See ClimaDry II submittal for application details and unit availability.)

Option: VFLow® — The unit will be supplied with internally factory mounted modulating water valve with ∆T control. The factory built-in valve shall modulate water flow through unit based on a field adjustable water temperature difference between the entering and leaving water. The valve shall automatically adjust for operating mode, source water temperature and variations in external head pressure. The valve will also act as a shut-off valve to prevent water flow through the unit when the unit is not activated and will have a minimum position capability.

Drain Pan:

The drain pan shall be constructed of 304 stainless steel. This corrosion protection system shall meet the stringent 1,000-hour salt spray test per ASTM B117. Drain pan shall be fully insulated. Drain outlet shall be located at pan as to allow complete and unobstructed drainage of condensate. Drain pan outlet side field selectable/convertible. Drain outlet shall be connected from pan directly to FPT fitting. No hidden internal tubing extensions from pan outlet extending to unit casing (that can create drainage problems) will be accepted. The unit as standard will be supplied with solid-state electronic condensate overflow protection. Mechanical float switches will NOT be accepted.

Electrical:

A control box shall be located within the unit compressor compartment and shall contain a 75 VA transformer with load side circuit breaker protection, 24 volt activated, 3 pole compressor contactor, terminal block for thermostat wiring and solid-state controller for complete unit operation. Reversing valve and fan motor wiring shall be routed through this electronic controller. Units shall be name-plated for use with time delay fuses or HACR circuit breakers. Unit controls shall be 24 Volt and provide heating or cooling as required by the remote thermostat/sensor. Two compressor units shall have a solid-state time delay relay and random start to prevent both compressors from starting simultaneously.

Option: Disconnect Switch, Non-Fused

Option: Disconnect Switch, Non-Fused and unpowered 115 VAC GFI convenience outlet (separate 115 VAC circuit required by others).

Option: Circuit Breaker

Option: Circuit Breaker and unpowered 115 VAC GFI convenience outlet (separate 115 VAC circuit required by others).

Outdoor Air:

The unit shall be supplied as standard with no outdoor air provisions (100% return air).

Option: Manual outside air damper with rain hood and bird screen sized for a maximum capacity of 20% of the total unit air volume for outside air volume.

Option: Two-position motorized outside air damper (opens outside air damper upon compressor contactor activation).

Option: Fully modulating enthalpy controlled economizer, supplied with large diameter ABS gear driven outdoor air and return air dampers. Solid-state economizer logic module shall be Honeywell W7220 series with Honeywell M7215 actuator. The economizer package shall also be supplied with gravity relief damper.

Option: Optional demand control ventilation when optional CO2 sensor is added to economizer.

Enhanced Solid State Control System (DXM2):

This control system is a communicating controller; also features two stage control of cooling and two stage control of heating modes for exacting temperature and dehumidification purposes.

This control system, coupled with a multi-stage thermostat, will better dehumidify room air by automatically running the heat pump’s fan at lower speed on the first stage of cooling thereby implementing low sensible heat ratio cooling. On the need for higher cooling performance, the system will activate the second stage of cooling and automatically switch the fan to the higher fan speed setting. This system may be further enhanced with a humidistat. Units not having automatic low sensible heat ration cooling will not be accepted; as an alternative, a hot gas reheat coil may be provided with control system for automatic activation.

Control features:

a.	Anti-short cycle time delay on compressor operation.

b.	Random start on power up mode.

c.	Low voltage protection.

d.	High voltage protection.

e.	Unit shutdown on high or low refrigerant pressures.

f.	Unit shutdown on low water temperature.

g.	Condensate overflow electronic protection.

h.	Option to reset unit at thermostat or disconnect.

i.	Automatic intelligent reset. Unit shall automatically reset the unit 5 minutes after trip if the fault has cleared. If a fault occurs 3 times sequentially without thermostat meeting temperature, then lockout requiring manual reset will occur.

j.	Ability to defeat time delays for servicing.

k.	Light emitting diode (LED) on circuit board to indicate high pressure, low pressure, low voltage, high voltage, low water/air temperature cut-out, condensate overlfow, and control voltage status.

l.	The low pressure switch shall not be monitored for the first 120 seconds after a compressor start command to prevent nuisance safety trips.

m.	24 V output to cycle a motorized water valve or other device with compressor contactor.

n.	Unit Performance Sentinel (UPS). The UPS warns when the heat pump is running inefficiently.

o.	Water coil low temperature sensing (selectable for water or anti-freeze).

p.	Air coil low temperature sensing.

q.	Removable thermostat connector.

r.	Night setback control.

s.	Random start on return from night setback.

t.	Minimized reversing valve operation (Unit control logic shall only switch the reversing valve when cooling is demanded for the

first time. The reversing valve shall be held in this position until the first call for heating, ensuring quiet operation and increased valve life).

u.	Override temperature control with 2-hour timer for room occupant to override setback temperature at the thermostat.

v.	Dry contact night setback output for digital night setback thermostats.

w.	Ability to work with heat pump or heat/cool (Y, W) type thermostats.

x.	Ability to work with heat pump thermostats using O or B reversing valve control.

y.	Emergency shutdown contacts.

z.	Boilerless system heat control at low loop water temperature.

aa.	Ability to allow up to 3 units to be controlled by one thermostat.

bb.	Relay to operate an external damper.

cc.	Ability to automatically change fan speed from multi-stage thermostat.

dd.	Relay to start system pump.

ee.	75 VA control transformer. Control transformer shall have load side short circuit and overload protection via a built in circuit breaker.

NOTE: Units not providing the 8 safety protections of anti-short cycle, low voltage, high voltage, high refrigerant pressure, low pressure (loss of charge), air coil low temperature cut-out, water coil low temperature cut-out, and condensate overflow protections will not be accepted.

NOTE: To achieve full benefit of the two-stage compressor and ECM fan, a 2 Heat/2 Cool thermostat (or a 3 Heat/2 Cool thermostat when electric backup heat is required) should be employed.

When DXM2 is connected to either ACDU service tool or ATC32U thermostat, the installer/service technician can; check all physical inputs from thermostat and refrigerant pressure switches status, (Y1, Y2, W, O, G, H, ESD, NSB, OR, HP switch, and LOC switch); current or at time of fault the following temperatures -LT1, LT2, compressor discharge, leaving air, leaving water, entering water and control voltage; record last five faults, list possible reasons, and clear faults.

Digital Night Setback with Pump Restart (DXM2 w/ATP32U03C/04C, ATC32U03C):

The unit will be provided with a Digital Night Setback feature using an accessory relay on the DXM2 controller with an ATP32U03C/04C thermostat and an external, field-provided time clock. The external time clock will initiate and terminate the night setback period. The thermostat will have a night setback override feature with a programmable override time period.

An additional accessory relay on the unit DXM2 controller will energize the building loop pump control for the duration of the override period. (Note: This feature requires additional low voltage wiring.  Consult Application Drawings for details.)

Remote Service Sentinel (DXM2):

Solid-state control system shall communicate with thermostat to display (at a compatible thermostat) the unit status, fault status, and specific fault condition, as well as retrieve previously stored fault that caused unit shutdown. The Remote Service Sentinel allows building maintenance personnel or service personnel to diagnose unit from the wall thermostat. The control board shall provide a signal to the thermostat fault light, indicating a lockout. Upon cycling the G (fan) input 3 times within a 60 second time period, the fault light shall display the specific code as indicated by a sequence of flashes. A detailed flashing code shall be provided at the thermostat LED to display unit status and specific fault status such as over/under voltage fault, high pressure fault, low pressure fault, low water temperature fault, condensate overflow fault, etc. Units that do not provide this remote service sentinel shall not be acceptable.

Option: MPC (Multiple Protocol Control) Interface System

Units shall have all the features listed above and the control board will be supplied with a Multiple Protocol interface board. Available protocols are BACnet MS/TP, Modbus, or Johnson Controls N2. The choice of protocol shall be field selectable/changeable via the use of a simple selector switch. Protocol selection shall not require any additional programming or special external hardware or software tools. This will permit all units to be daisy chain connected by a 2-wire twisted pair shielded cable. The following points must be available at a central or remote computer location:

a.	Space temperature

b.	Leaving water temperature

c.	Discharge air temperature

d.	Command of space temperature setpoint

e.	Cooling status

f.	Heating status

g.	Low temperature sensor alarm

h.	Low pressure sensor alarm

i.	High pressure switch alarm

j.	Condensate overflow alarm

k.	Hi/low voltage alarm

l.	Fan “ON/AUTO” position of space thermostat as specified above

m.	Unoccupied/occupied command

n.	Cooling command

o.	Heating command

p.	Fan “ON/AUTO” command

q.	Fault reset command

r.	Itemized fault code revealing reason for specific shutdown fault (any one of 7)

This option also provides the upgraded 75 VA control transformer with load side short circuit and overload protection via a built in circuit breaker.

Warranty:

ClimateMaster shall warranty equipment for a period of 12 months from start up or 18 months from shipping (which ever occurs first).

Option: Extended 4-year compressor warranty covers compressor for a total of 5 years.

Option: Extended 4-year refrigeration circuit warranty covers coils, reversing valve, expansion valve and compressor for a total of 5 years.

Option: Extended 4-year control board warranty covers the CXM/DXM2 control board for a total of 5 years.

FIELD INSTALLED OPTIONS

Thermostats:

The thermostat shall be a ClimateMaster mechanical or electronic type thermostat as selected below with the described features:

a.	Thermostat (communicating) (ATC32U01)

An electronic communicating LCD thermostat shall be provided. The thermostat shall offer three stages of heating and two stages of cooling with precise temperature control and have a four-wire connection to the unit. The thermostat shall be capable of manual or automatic change-over operation and shall operate in standard or programmable mode. An integrated humidity control feature shall be included to control a humidifier and/or a dehumidifier. The thermostat shall include a utility demand reduction feature to be initiated by an independent time program or an external input.

The thermostat shall have a comprehensive installation setup menu to include configuration of the unit CFM for each mode of operation and configuration of the water flow rate through the unit, including variation of the water flow rate based on the stage of unit operation.

The thermostat shall display system faults with probably cause and troubleshooting guidance. Comprehensive service diagnostics menus shall display: system inputs, system outputs, configuration settings, Geo source inlet and outlet temperatures, compressor discharge line temperature, liquid line temperature, leaving air temperature, and entering potable water temperature (on units equipped with a Hot Water Generator). The thermostat shall allow for immediate manual control of all DXM2 outputs at the thermostat for rapid troubleshooting.

b.	Multi-stage Digital Automatic Changeover (ATA22U01)

Thermostat shall be multi-stage (2H/2C), manual or automatic changeover with HEAT-OFF-COOL-AUTO-EM HEAT system settings and fan ON-AUTO settings. Thermostat shall have an LCD display with temperature, setpoint(s), mode, and status indication. The temperature indication shall be selectable for ºF or ºC. The thermostat shall provide permanent memory of setpoint(s) without batteries. A fault LED shall be provided to indicate specific fault condition(s). Thermostat shall provide temperature display offset for custom applications. Thermostat shall allow unit to provide better dehumidification with optional DXM2 controller by automatically using lower fan speed on stage 1 cooling (higher latent cooling) as main cooling mode, and automatically shifting to high-speed fan on stage 2 cooling.

c.	Multi-stage Manual Changeover Programmable 5/2 Day (ATP21U01)

Thermostat shall be 5 day/2 day programmable (with up to 4 setpoints per day), multi-stage (2H/1C), manual changeover with HEAT-OFF-COOL-EM HEAT system settings and fan ON-AUTO settings. Thermostat shall have an LCD display with temperature, setpoint(s), mode, and status indication. The temperature indication shall be selectable for ºF or ºC. The thermostat shall provide permanent memory of setpoint(s) without batteries. Thermostat shall provide convenient override feature to temporarily change setpoint.

d.	Multi-stage Automatic or Manual Changeover Programmable 7 Day (ATP32U03)

Thermostat shall be 7 day programmable (with up to 4 setpoints per day), multi-stage (3H/2C), automatic or manual changeover with HEAT-OFF-COOL-AUTO-EM HEAT system settings and fan ON-AUTO settings. Thermostat shall have a blue backlit dot matrix LCD display with temperature, setpoints, mode, and status indication. The temperature indication shall be selectable for ºF or ºC. Time display shall be selectable for 12 or 24 hour clock. Fault identification shall be provided (when used with ClimateMaster CXM or DXM2 controls) to simplify troubleshooting by providing specific unit fault at the thermostat with red backlit LCD during unit lockout. The thermostat shall provide permanent memory of setpoints without batteries. Thermostat shall provide heating setpoint range limit, cooling setpoint range limit, temperature display offset, keypad lockout, dead-band range setting, and inter-stage differential settings. Thermostat shall provide progressive recovery to anticipate time required to bring space temperature to the next programmed event. Thermostat shall provide an installer setup for configuring options and for setup of servicing contractor name and contact information. Thermostat shall allow the use of an accessory remote and/or outdoor temperature sensor (AST008). Thermostat navigation shall be accomplished via five buttons (up/down/right/left/select) with menu-driven selections for ease of use and programming.

e.  Multi-stage Automatic or Manual Changeover Programmable 7 Day with Humidity Control

(ATP32U04)

Thermostat shall be 7 day programmable (with up to 4 setpoints per day), multi-stage (3H/2C), automatic or manual changeover with HEAT-OFF-COOL-AUTO-EM HEAT system settings and fan ON-AUTO settings. Separate dehumidification and humidification setpoints shall be configurable for discreet outputs to a dehumidification option and/or an external humidifier. Installer configuration mode shall allow thermostat dehumidification mode to operate with ClimaDry® reheat or with ECM fan dehumidification mode via settings changes. Thermostat shall have a blue backlit dot matrix LCD display with temperature, relative humidity, setpoints, mode, and status indication. The temperature indication shall be selectable for ºF or ºC. Time display shall be selectable for 12 or 24 hour clock. Fault identification shall be provided (when used with ClimateMaster CXM or DXM2 controls) to simplify troubleshooting by providing specific unit fault at the thermostat with red backlit LCD during unit lockout. The thermostat shall provide permanent memory of setpoints without batteries. Thermostat shall provide heating setpoint range limit, cooling setpoint range limit, temperature display offset, keypad lockout, dead-band range setting, and inter-stage differential settings. Thermostat shall provide progressive recovery to anticipate time required to bring space temperature to the next programmed event. Thermostat shall provide an installer setup for configuring options and for setup of servicing contractor name and contact information. Thermostat shall allow the use of an accessory remote and/or outdoor temperature sensor (AST008). Thermostat navigation shall be accomplished via five buttons (up/down/right/left/select) with menu-driven selections for ease of use and programming.

DDC Sensors:

ClimateMaster wall mounted DDC sensor to monitor room temperature and interfaces with optional interface system described above. Several types as described below:

a.	Sensor only with no display (MPC).

b.	Sensor with setpoint adjustment and override (MPC only).

c.	Sensor with setpoint adjustment and override, LCD display, status/fault indication (MPC).

Roof Curbs:

# A 14 inch (356 mm) high knockdown roof curb for flat roofs is available as standard in down discharge configuration. Other curbs are available by special request.

# Text boxes

# TRANQUILITY® ROOFTOP “TRT” 036-072 60 Hz

# ENGINEERING SPECIFICATIONS

This product specification document is furnished as a means to copy and paste ClimateMaster product information into project specification. It is not intended to be a complete list of product requirements. This document is an excerpt from the product submittal and must not be used without consulting the complete product submittal. For complete product installation and application requirements, please consult the complete product submittal. ClimateMaster is not responsible for misuse of this document or a failure to adequately review specific requirements in the product submittal.